ALMA Test Interferometer Holography Tower

R.  Sramek - November 15, 2001

A. Tower Specifications:

1)  Height, nominal		160 ft

2)  Survival wind speed, no ice		110 mph

Survival wind speed with 1/2" solid radial ice 	83 mph

(per ANSI / EIA-222-F)

3)  FAA obstruction lighting 	Red only, placement as per FCC circular AC70/7460-1K

4)  Electrical power	120 VAC available on tower (see section C-4 )

a) three independent circuits, installed in metal conduit, to supply:

1.  NRAO 3mm transmitter box and utility power, approx 300 W, at top of tower;

2. Heat lamp, approx 500 W,  at top of tower;

3. FAA obstruction lighting, approx 400 W.

b) circuits 1. and 2. will terminate in a weatherproof junction box mounted on the tower top plate.  The heat lamp will be mounted on this junction box.  The junction box and heat lamp will be supplied by NRAO and installed by contractor.

c) the three circuits may share a conduit

5) Fiber optic signal cable	approx 1/2 inch cable, supplied by owner, installed by contractor from base of tower to top plate

6) A mounting plate for the 3mm transmitter will be supplied by NRAO and installed by contractor on the top plate.  NRAO will supply a layout for the tower top plate.

7)  Lateral peak-to-peak movement 	<0.4 inch (10 mm) at top of tower, with 20 mph wind speed measured at 35 feet elevation.  Deflection measuring system to be agreed upon.

8) NRAO equipment (3mm transmitter with mounting plate, heat lamp and power junction box) to be  mounted at top of tower:

Load 	< 40 lbs

Vertical surface area 	< 2 sq ft in any projection

9) Lightning protection	Three lightning rods with a single bare copper conductor (#2 AWG) running to base of tower and connected to grounding system (rods supplied by owner).

10)   Fabrication and installation shall be in accordance with ANSI / EIA-222-F and NEC.

B.  Deliverables

Quote should include the following deliverables:

1) Design drawings and calculations in accordance with specifications.

2) Foundation and anchor designs

3) All tower, guying materials and accessories as called for in specifications

4) Base plate and guying connecting hardware

5) Tower top plate

6) Electrical grounding kits for tower base and guy anchors

7) OSHA approved climbing ladder and fall protection equipment

8) Construction of foundations for the tower and guy anchors, including grounding system

9) Installation of tower at VLA site with guy alignment as shown in drawing

10) Chain link fence, 6ft, around tower and guy anchors

11) Field inspection and sign-off by manufacturers representative that construction meets requirements of  ANSI / EIA-222-F and NEC.

C.  Supplied by NRAO

1) Soil tests at tower site; will be distributed 2 weeks before bid due date

2) Any necessary permits or exemptions

3) Notify FAA and USAF of tower height, location and radiated rf emission.

4) Electrical power (120 VAC ) to base of tower, terminating in a weatherproof breaker box, with lightning arresters and three 20 A circuit breakers.  Receptacles for 120 VAC utility power will be provided here.

5) For installation at top of tower:

a) 120 VAC junction box (includes heat lamp, utility receptacles, and weatherproof 120 VAC connectors for 3mm transmitter).

b) 3mm transmitter box with mounting plate

6) Fiber optic signal cable to base of tower plus 170 free cable with weatherproof connector.